## COT-Q1
COT for 1 x 10 MW unit
| FOR | 0.02 |  | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Load Loss | Expected Load Loss | System | Loss of Load Probability | Expected Load Curtailment
| Load | 10 |  | 1 | 0.02 | 0 | 0 | 10 | 0.98 | 0 | 0 | 1x10 | 0.02 | 175.2
| No. | Capacity | Total | 1 | 0.02 | 1 | 10 | 0 | 0.02 | 10 | 0.2 | 2x10 | 0.0004 | 35.04
(a) | 1 | 10 | 10 | [5 empty] | 1 |  | 0.2 | 3x5 | 0.001184 | 103.7184
(b) | 2 | 10 | 20 |  |  | COT for 2 x 10 MW unit | [5 empty] | 4x3(1/3) | 0.0023365 | 204.6756
( c) | 3 | 5 | 15 | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Load Loss | Expected Load Loss
(d) | 4 | 3.3333 | 13.3333 | 2 | 0.02 | 0 | 0 | 20 | 0.9604 | 0 | 0
|  |  |  | 2 | 0.02 | 1 | 10 | 10 | 0.0392 | 0 | 0
|  |  |  | 2 | 0.02 | 2 | 20 | 0 | 0.0004 | 10 | 0.004
[9 empty] | 1 |  | 0.004
COT for 3 x 5 MW units
|  |  |  | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Load Loss | Expected Load Loss
|  |  |  | 3 | 0.02 | 0 | 0 | 15 | 0.94119 | 0 | 0
|  |  |  | 3 | 0.02 | 1 | 5 | 10 | 0.057624 | 0 | 0
|  |  |  | 3 | 0.02 | 2 | 10 | 5 | 0.001176 | 5 | 0.00588
|  |  |  | 3 | 0.02 | 3 | 15 | 0 | 8e-06 | 10 | 8e-05
[9 empty] | 1 |  | 0.00596
COT for 4 x 3.333 MW units
|  |  |  | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Load Loss | Expected Load Loss
|  |  |  | 4 | 0.02 | 0 | 0 | 13.3333 | 0.92237 | 0 | 0
|  |  |  | 4 | 0.02 | 1 | 3.3333 | 10 | 0.075295 | 0 | 0
|  |  |  | 4 | 0.02 | 2 | 6.6667 | 6.6667 | 0.002305 | 3.3333 | 0.0076832
|  |  |  | 4 | 0.02 | 3 | 10 | 3.3333 | 3.136e-05 | 6.6667 | 0.00020907
|  |  |  | 4 | 0.02 | 4 | 13.3333 | 0 | 1.6e-07 | 10 | 1.6e-06
[9 empty] | 1 |  | 0.0078939

## COT-Q2
Non Identical Units
FOR (5 MW) | 0.02 |  |  |  | COT for 3 MW unit
Unit (MW) | No. | Total (MW) | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Capacity Out (MW) | MW Available | Individual Probability | Cumulative Probability
3 | 2 | 6 | 2 | 0.02 | 0 | 0 | 6 | 0.9604 | 0 | 11 | 0.94119 | 1
|  |  | 2 | 0.02 | 1 | 3 | 3 | 0.0392 | 3 | 8 | 0.038416 | 0.058808
|  |  | 2 | 0.02 | 2 | 6 | 0 | 0.0004 | 5 | 6 | 0.019208 | 0.020392
[5 empty] | Addition of 5 MW unit in service |  |  |  | 6 | 5 | 0.000392 | 0.001184
[6 empty] | 0 |  | 0.94119 | 8 | 3 | 0.000784 | 0.000792
[6 empty] | 3 |  | 0.038416 | 11 | 0 | 8e-06 | 8e-06
[6 empty] | 6 |  | 0.000392
0.98
Addition of 5 MW unit out of service
[6 empty] | 5 |  | 0.019208
[6 empty] | 8 |  | 0.000784
[6 empty] | 11 |  | 8e-06
0.02

## COT-Q3
COT for System-1
System | Unit Capacity | No of Units | Total Capacity | FOR | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Cumulative Probability
1 | 10 | 24 | 240 | 0.01 | 24 | 0.01 | 0 | 0 | 240 | 0.78568 | 1
2 | 20 | 12 | 240 | 0.01 | 24 | 0.01 | 1 | 10 | 230 | 0.19047 | 0.21432
3 | 20 | 12 | 240 | 0.03 | 24 | 0.01 | 2 | 20 | 220 | 0.022125 | 0.023854
4 | 10 | 22 | 220 | 0.01 | 24 | 0.01 | 3 | 30 | 210 | 0.0016389 | 0.0017293
[5 empty] | 24 | 0.01 | 4 | 40 | 200 | 8.6911e-05 | 9.0422e-05
[5 empty] | 24 | 0.01 | 5 | 50 | 190 | 3.5115e-06 | 3.5115e-06
COT for System-2
[5 empty] | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Cumulative Probability
[5 empty] | 12 | 0.01 | 0 | 0 | 240 | 0.88638 | 1
[5 empty] | 12 | 0.01 | 1 | 20 | 220 | 0.10744 | 0.11362
[5 empty] | 12 | 0.01 | 2 | 40 | 200 | 0.0059689 | 0.0061745
[5 empty] | 12 | 0.01 | 3 | 60 | 180 | 0.00020097 | 0.00020554
[5 empty] | 12 | 0.01 | 4 | 80 | 160 | 4.5676e-06 | 4.5676e-06
COT for System-3
[5 empty] | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Cumulative Probability
[5 empty] | 12 | 0.03 | 0 | 0 | 240 | 0.69384 | 1
[5 empty] | 12 | 0.03 | 1 | 20 | 220 | 0.25751 | 0.30616
[5 empty] | 12 | 0.03 | 2 | 40 | 200 | 0.043803 | 0.048649
[5 empty] | 12 | 0.03 | 3 | 60 | 180 | 0.0045158 | 0.0048461
[5 empty] | 12 | 0.03 | 4 | 80 | 160 | 0.00031424 | 0.00033035
[5 empty] | 12 | 0.03 | 5 | 100 | 140 | 1.555e-05 | 1.6111e-05
[5 empty] | 12 | 0.03 | 6 | 120 | 120 | 5.6109e-07 | 5.6109e-07
COT for System-4
[5 empty] | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Cumulative Probability
[5 empty] | 22 | 0.01 | 0 | 0 | 220 | 0.80163 | 1
[5 empty] | 22 | 0.01 | 1 | 10 | 210 | 0.17814 | 0.19837
[5 empty] | 22 | 0.01 | 2 | 20 | 200 | 0.018894 | 0.020229
[5 empty] | 22 | 0.01 | 3 | 30 | 190 | 0.0012723 | 0.0013356
[5 empty] | 22 | 0.01 | 4 | 40 | 180 | 6.1045e-05 | 6.3264e-05
[5 empty] | 22 | 0.01 | 5 | 50 | 170 | 2.2198e-06 | 2.2198e-06