## LOLE-Q1
FOR (50 MW) | 0.02 |  |  |  | COT for 25 MW units |  |  |  | COT for the system |  |  |  | Loss of Load Expectation
Unit (MW) | No. | Total (MW) | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Capacity Out (MW) | MW Available | Individual Probability | Cumulative Probability | Capacity Ci | Peak Load Li | No of Occur | Ci - Li | Prob (Ci-Li) | LOLE
25 | 2 | 50 | 2 | 0.02 | 0 | 0 | 50 | 0.9604 | 0 | 100 | 0.94119 | 1 | 100 | 57 | 12 | 43 | 0.020392 | 0.2447
50 | 1 | 50 | 2 | 0.02 | 1 | 25 | 25 | 0.0392 | 25 | 75 | 0.038416 | 0.058808 | 100 | 52 | 83 | 48 | 0.020392 | 1.6925
|  | 100 | 2 | 0.02 | 2 | 50 | 0 | 0.0004 | 50 | 50 | 0.0196 | 0.020392 | 100 | 46 | 107 | 54 | 0.000792 | 0.084744
[5 empty] | Addition of 50 MW unit in service |  |  |  | 75 | 25 | 0.000784 | 0.000792 | 100 | 41 | 116 | 59 | 0.000792 | 0.091872
[6 empty] | 0 |  | 0.94119 | 100 | 0 | 8e-06 | 8e-06 | 100 | 34 | 47 | 66 | 0.000792 | 0.037224
[6 empty] | 25 |  | 0.038416 | [9 empty] | 2.1511
[6 empty] | 50 |  | 0.000392 | [9 empty] | days/year
0.98
Addition of 50 MW unit out of service
[6 empty] | 50 |  | 0.019208
[6 empty] | 75 |  | 0.000784
[6 empty] | 100 |  | 8e-06
0.02
Note on U5: Capacity Outage greater than this will result in loss of load
Note on V5: Probability of capacity outage for loss of load

## LOLE-Q1-Dir
Theare are some issues in direct computation as the cumulative probability is different from that provided in the book.
Capacity Outage Table (Direct Probability Method)
System | Unit Capacity | No of Units | Total Capacity | FOR | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Cumulative Probability | Book Answer
1 | 25 | 1 | 25 | 0.02 | 3 | 0.01 | 0 | 0 | 100 | 0.94119 | 1.0024 | 1
2 | 25 | 1 | 25 | 0.02 | 3 | 0.01 | 25 or 25 | 25 | 75 | 0.04 | 0.061208 | 0.58808
3 | 50 | 1 | 50 | 0.02 | 3 | 0.01 | two 25 or one 50 | 50 | 50 | 0.0204 | 0.021208 | 0.20392
|  |  | 100 |  | 3 | 0.01 | one 25 one 50 | 75 | 25 | 0.0008 | 0.000808 | 0.000792
[5 empty] | 3 | 0.01 | two 25 and one 50 | 100 | 0 | 8e-06 | 8e-06 | 8e-06

## LOLE-Q2
Capacity Outage Table for 5 x40 MW system
Unit (MW) | No. | Total (MW) | Total Units | FOR | Units Out | Capacity Out | MW Available | Individual Probability | Cumulative Probability | Total Time tk (%) | LOLE (%)
40 | 5 | 200 | 5 | 0.01 | 0 | 0 | 200 | 0.95099 | 1 | - | -
|  |  | 5 | 0.01 | 1 | 40 | 160 | 0.04803 | 0.04901 | - | -
|  |  | 5 | 0.01 | 2 | 80 | 120 | 0.0009703 | 0.00098015 | 41.7 | 0.040461
|  |  | 5 | 0.01 | 3 | 120 | 80 | 9.801e-06 | 9.8505e-06 | 83.4 | 0.0008174
Peak | 160 | MW | 5 | 0.01 | 4 | 160 | 40 | 4.95e-08 | 4.95e-08 | Neglected
Load | Time | Slope | [5 empty] | 1 |  |  | 0.041279 | (%)
160 | 0 | -0.96 | [8 empty] | 0.15067 | days
64 | 100 | [9 empty] | 6.6371 | years per day
120 | 41.6667
80 | 83.3333

## LOLE-Q3
Capacity Outage Table for 5 x40 MW system
Unit (MW) | No. | Total (MW) | Total Units | FOR | Units Out | Capacity Out (Ok) | MW Available | Individual Probability | Cumulative Probability | Total Time tk (%) | Ek (Ok*tk) | Ek*Pk
40 | 5 | 200 | 5 | 0.01 | 0 | 0 | 200 | 0.95099 | 1 | - | 0 | 0
|  |  | 5 | 0.01 | 1 | 40 | 160 | 0.04803 | 0.04901 | - | 0 | 0
|  |  | 5 | 0.01 | 2 | 80 | 120 | 0.0009703 | 0.00098015 | 0.417 | 33.36 | 0.032369
|  |  | 5 | 0.01 | 3 | 120 | 80 | 9.801e-06 | 9.8505e-06 | 0.834 | 100.08 | 0.00098088
Peak | 160 | MW | 5 | 0.01 | 4 | 160 | 40 | 4.95e-08 | 4.95e-08 | Neglected
Load | Time | Slope | [5 empty] | 1 |  |  | 133.44 | 0.03335
160 | 0 | -0.96
64 | 100 | [8 empty] | LOEE | 0.03335
120 | 41.6667 | [8 empty] | LOEEpu | 0.00029777
80 | 83.3333 | [8 empty] | EIR | 0.9997
[9 empty] | Total Energy under LDC |  | 112

## EENS
|  |  | EENS with Unit-1 (Installed Capacity 25 MW) | [5 empty] | Summary of EENS
Unit | Capacity (MW) | Probability | Capacity out of Service (MW) | Capacity in Service (MW) | Prob | Energy Curtailed (MWh) | Expectation (MWh) |  | Priority Level | Unit Capacity (MW) | EENS (MWh) | Expected Energy Output (MWh)
1 | 0 | 0.05 | 0 | 25 | 0.65 | 2075 | 1348.75 |  | 1 | 25 | 2500 | 2075
| 15 | 0.3 | 10 | 15 | 0.3 | 3075 | 922.5 |  | 2 | 30 | 401.7154 | 2098.2846
| 25 | 0.65 | 25 | 0 | 0.05 | 4575 | 228.75 |  | 3 | 20 | 64.06 | 337.6554
2 | 0 | 0.03 |  |  |  | EENS1 | 2500 | MWh
| 30 | 0.97
3 | 0 | 0.04 | Expected Energy produced by Unit-1 |  |  |  | 2075 | MWh
| 20 | 0.96
EENS0 | 4575 | MWh | EENS with Unit-1 and 2 (Installed Capacity 55 MW)
|  |  | Capacity out of Service (MW) | Capacity in Service (MW) | Prob | Energy Curtailed (MWh) | Expectation (MWh)
|  |  | 0 | 55 | 0.6305 | 177.8 | 112.1029
|  |  | 10 | 45 | 0.291 | 475 | 138.225
|  |  | 25 | 30 | 0.0485 | 1575 | 76.3875
|  |  | 30 | 25 | 0.0195 | 2075 | 40.4625
|  |  | 40 | 15 | 0.009 | 3075 | 27.675
|  |  | 55 | 0 | 0.0015 | 4575 | 6.8625
[6 empty] | EENS2 | 401.7154 | MWh
|  |  | Expected Energy produced by Unit-1 |  |  |  | 2098.2846 | MWh
EENS with Unit-1 and 2 (Installed Capacity 75 MW)
|  |  | Capacity out of Service (MW) | Capacity in Service (MW) | Prob | Energy Curtailed (MWh) | Expectation (MWh)
|  |  | 0 | 75 | 0.60528 | 0 | 0
|  |  | 10 | 65 | 0.27936 | 44.4 | 12.4036
|  |  | 20 | 55 | 0.02522 | 177.8 | 4.4841
|  |  | 25 | 50 | 0.04656 | 286 | 13.3162
|  |  | 30 | 45 | 0.03036 | 475 | 14.421
|  |  | 40 | 35 | 0.00864 | 1119.4 | 9.6716
|  |  | 45 | 30 | 0.00194 | 1575 | 3.0555
|  |  | 50 | 25 | 0.00078 | 2075 | 1.6185
|  |  | 55 | 20 | 0.00144 | 2575 | 3.708
|  |  | 60 | 15 | 0.00036 | 3075 | 1.107
|  |  | 75 | 0 | 6e-05 | 4575 | 0.2745
[6 empty] | EENS3 | 64.06 | MWh
|  |  | Expected Energy produced by Unit-1 |  |  |  | 337.6554 | MWh
Note on K17: How?
Note on K18: How?
Note on K30: How?
Note on K31: How?